READ THIS FIRST

Notice to the Design Engineer, please refer to the Port of Seattle, Facilities and Infrastructure standards for reference before editing this specification.

This Project Spec Document may need additional modifications to suit your project. It is recommended that you proofread each section, paying attention to any “Notes” boxes such as this one--you should remove these “Notes” sections as you go. Also, do a search for all bracket characters “ [ ] “ as they are used to show you areas containing options or project specific details (you can use Microsoft Word’s Find feature {Ctrl-F} to jump to an open bracket “ [ “ character quickly). Again, these bracket characters should be removed.

It is important that every paragraph be numbered to allow for easy referencing. If you use the document’s built in styles and formatting your outline should be fine (turn on the formatting toolbar by going to View > Toolbars > Formatting). Most paragraphs will use the style “Numbered Material” and can be promoted (Shift) or demoted (Shift-Tab).

You should not have to manually enter extra spaces, carriage returns or outline characters such as A, B, C, or 1.01, 1.02; the formatting will do this for you. The entire document is 11 pt. Arial. If you paste items in, you may need to reapply the “Numbered Material” format.

- GENERAL

  - SUMMARY OF WORK

    - The extent and location of “Lighting Control Devices” Work is shown in the Contract Documents. This section includes the following:

Lighting controls shall be provided to comply with Washington State Non-residential Energy Code at a minimum. STIA is a 24-hour facility and public spaces are exempt from automatic off controls.

Occupancy Vacancy sensors are required in all conference rooms with override capability. Such sensors shall be dual technology to decrease the number of false empty-room errors.

Lighting in daylight zones will be dual level switched or dimmed, per WSEC.

      - Time switches.

      - Time clocks.

      - Outdoor photoelectric switches.

      - Daylight harvesting dimming controls.

      - Indoor occupancy/vacancy sensors.

      - Lighting contactors.

      - Emergency shunt relays.

  - GOVERNING CODES, STANDARDS AND REFERENCES

    - 47 CFR 15: Radio Frequency Devices, Subparts A: General and B: Unintentional Radiators

    - NECA 1: Good Workmanship in Electrical Construction

    - NEMA 250: Enclosures for Electrical Equipment (1000 Volts Maximum)

    - NEMA ICS 2: Industrial Control and Systems: Controllers, Contactors, and Overload Relays Rated 600 Volts

    - NFPA 70 (National Fire Protection Association) - National Electrical Code,

    - NFPA 101 (National Fire Protection Association) - Life Safety Code,

    - Washington State Non-residential Energy Code

    - UL (Underwriters Laboratory)

    - UL 508: Industrial Control Equipment

    - UL 773A: Standard for Nonindustrial Photoelectric Switches for Lighting Control

    - UL 924: Standard for Emergency Lighting and Power Equipment.

  - SUBMITTALS

    - Submit materials data in accordance with of Section 01 33 00 - Submittals. Furnish manufacturers’ technical literature, standard details, product specifications, and installation instructions for all products.

    - Submittals shall include the following:

      - Product Data: Include dimensions and data on features, components, and ratings for lighting control devices.

      - Shop Drawings: Show installation details for occupancy and light-level sensors.

        - Interconnection diagrams showing field-installed wiring.

        - Include diagrams for power, signal, and control wiring.

      - Field Test Reports: Indicate and interpret test results for compliance with performance requirements.

      - Commissioning plan with test procedures.

      - Operations and Maintenance Data: For each type of lighting control device to include in maintenance manuals specified in Division 1 General Requirements. Include operation and maintenance manuals.

      - Warranties: Special warranties specified in this section.

  - QUALITY ASSURANCE

    - Listing and Labeling: Provide electrical components, devices, and accessories that are Listed and Labeled as defined in NFPA 70, Article 100 and marked for intended use for the location and environment in which they are installed.

    - Comply with NFPA 70, as adopted and administered by the Authority Having Jurisdiction.

  - WARRANTY

    - General Warranty: Special warranty specified in this Article shall not deprive Owner of other rights Owner may have under other provisions of the Contract Documents and shall be in addition to, and run concurrent with, other warranties made by Contractor under requirements of the Contract Documents.

    - Special Warranty: Written warranty, executed by manufacturer agreeing to repair or replace components of dimming controls that fail in materials or workmanship within specified warranty period.

Below is an example only. Verify available warranties and length of warranty period with manufacturers selected.

    - Warranty Period: Two years from date of Substantial Completion.

- PRODUCTS

A.	If only one product is acceptable (single or sole source product), obtain an approved Competition Waiver and submit to the CPO Construction, Contract Administrator.  The language shall read as: “Manufacturer Name, Product # XXXXX, No Equal.”  Refer to CPO-6 Competition Waiver Policy for more information.

B.	If a Competition Waiver is not approved or more than one product is acceptable, this section must list a minimum of 2 products plus the language “Or Approved Equal,” along with salient characteristics.  Refer to CPO Construction’s Salient Characteristics Guidelines for more information.

  - MANUFACTURERS

    - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

      - Time Switches

        - Intermatic, Inc.

        - Leviton Manufacturing Co., Inc.

        - NSi Industries LLC; TORK Products.

        - Or Approved Equal

      - Time Clocks

        - Intermatic

        - NSi Industries LLC; Tork

        - Paragon

        - Or Approved Equal

      - Outdoor Photoelectric Switches

        - Intermatic, Inc

        - NSI Industries LLC; TORK

        - Or Approved Equal.

      - Daylight-Harvesting Dimming Controls

        - Sensor Switch

        - Hubbell Building Automation, Inc.

        - Leviton Mfg. Company Inc

        - Watt Stopper

        - Acuity Brands

        - Or Approved Equal

      - Indoor Occupancy/Vacancy Sensors

        - Leviton Manufacturing Co., Inc.

        - Lutron Electronics Co., Inc.

        - Sensor Switch, Inc.

        - Watt Stopper.

        - Acuity Brands.

        - Or Approved Equal

      - Switch Box Mounted Occupancy Sensors

        - Leviton Manufacturing Co., Inc.

        - Lutron Electronics Co., Inc.

        - NSi Industries LLC; TORK Products.

        - Sensor Switch, Inc.

        - Watt Stopper.

        - Acuity Brands.

        - Or Approved Equal

      - Wall-Switch Sensor

        - Leviton Manufacturing Co. Inc

        - Lutron Electronics Co. Inc

        - Or Approved Equal

      - Lighting Contactors

        - Eaton Corporation

        - Square D.; Division of Schneider Electric.

        - General Electric.

        - Cutler-Hammer; Division of Eaton.

        - Allen Bradley.

        - Or Approved Equal.

      - Emergency Shunt Relay

        - Lighting Control and Design

        - Watt Stopper

        - LVS Controls

        - Or Approved Equal

  - TIME SWITCHES

    - Electronic Time Switches: Solid state, programmable, with alphanumeric display; programmable from 5 minutes to 24 hours.

      - Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

      - Battery Backup: Not less than seven days reserve, to maintain schedules and time clock.

  - TIME CLOCKS

    - Time Clock: Multi-purpose, microprocessor based digital controller with astronomical settings.

      - Eight channels.

      - 365-day advance single and block holiday scheduling.

      - Program entities shall be made by mechanical pushbutton and acknowledgement of each entry into the unit.

      - Remote timed override for each channel

      - Automatic daylight saving or standard time.

  - OUTDOOR PHOTOELECTRIC SWITCHES

    - Description: Solid state, with dry contacts rated for 1800-VA tungsten or 1000-VA inductive, to operate connected relay, contactor coils, or microprocessor input; complying with UL 773A.

    - Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

    - Light Level Monitoring Range:  1-5 fc on, 3-15fc off with an adjustment for turn-on and turn-off levels within that range. Per Washington State Administrative code (Non-residential Energy Code) or IES whichever is more stringent.

    - Time Delay: Up to two minutes to prevent false operation

    - Surge Protection: Metal-oxide varistor

    - Cell:  Cadmium sulfide, epoxy coated.

    - Contacts:  Closed between dusk and dawn.

    - Temperature range:  -40°F to 140°F.

    - Manual bypass switch shall be installed in parallel to the photocell. Keyed if accessible to general public.

    - For outdoor lighting, provide 60-minute timed on override in accessible location unless fog detection or time clock is included in photoelectric controller.

    - Enclosure:  Heavy-duty die cast zinc, gasketed for maximum weather protection.

    - Photoelectric cells shall typically be conduit mounted.

  - DAYLIGHT-HARVESTING DIMMING CONTROLS

    - System Description: Sensing daylight and electrical lighting levels, the system adjusts the indoor electrical lighting levels. As daylight increases, the lights are dimmed.

      - Lighting control set point is based on two lighting conditions:

        - When no daylight is present (target level).

        - When significant daylight is present.

      - System programming is done with two hand-held, remote-control tools.

        - Initial setup tool.

        - Tool for occupants to adjust the target levels by increasing the set point up to 25 percent, or by minimizing the electric lighting level.

    - Ceiling-Mounted Dimming Controls: Solid-state, light-level sensor unit, with separate controller unit, to detect changes in lighting levels that are perceived by the eye.

      - Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

      - Sensor Output: 0- to 10-V dc to operate electronic dimming ballasts. Sensor is powered by controller unit.

      - Power Pack: Sensor has 24-V dc, Class 2 power source, as defined by NFPA 70. Capable of controlling two separate zones of lighting based on input from single photosensor.

      - Light-Level Sensor Set-Point Adjustment Range: 3-6000 fc.

  - INDOOR OCCUPANCY/VACANCY SENSORS

    - General Requirements for Sensors: Wall- or ceiling-mounted, solid-state indoor occupancy sensors with a separate power pack.

      - Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

      - Operation: Unless otherwise indicated operation shall be as follows:

        - Occupancy Sensors:  Turn lights on when coverage area is occupied, and turn them off when unoccupied; with a time delay for turning lights off, adjustable over a minimum range of 1 to 30 minutes.

        - Vacancy Sensors:  Lights are turned on manually by occupant, and sensor turns them off when unoccupied; with a time delay for turning lights off, adjustable over a minimum range of 1 to 30 minutes.

      - Sensor Output: Contacts rated to operate the connected relay, complying with UL 773A. Sensor is powered from the power pack.

      - Power Pack: Dry contacts rated for 20-A ballast load at 120- and 277-V ac, for 13-A tungsten at 120-V ac, and for 1 hp at 120-V ac. Sensor has 24-V dc, 150-mA, and Class 2 power source, as defined by NFPA 70.

      - Mounting:

        - Sensor: Suitable for mounting in any position on a standard outlet box.

        - Relay: Externally mounted in a standard electrical enclosure.

        - Time-Delay and Sensitivity Adjustments: Recessed and concealed behind hinged door.

      - Indicator: LED status lights to show when motion is detected during testing and normal operation of sensor.

      - Bypass Switch: Override the "on" function in case of sensor failure.

    - Dual-Technology Type: Ceiling mounted; detect occupants in coverage area using PIR and ultrasonic detection methods. Trigger of either technology turns lights on. Both technologies must detect vacancy in order for lights to turn off.

      - Sensitivity Adjustment: Separate for each sensing technology.

      - Detector Sensitivity: Detect occurrences walking motion and desktop motion.

      - Detection Coverage: Provide sensor layout to ensure complete room coverage. Ceiling mounted sensors shall have 360° of coverage.

      - Ceiling sensor shall be used in conjunction with manual wall switch. Verify compatibility of sensor and wall switch.

      - Sensor shall be capable of manual on/auto off function.

  - SWITCHBOX-MOUNTED OCCUPANCY SENSORS

    - General Requirements for Sensors: Automatic-wall-switch occupancy sensor, suitable for mounting in a single gang switchbox.

      - Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

      - Operating Ambient Conditions: Dry interior conditions, 32 to 120 deg F.

      - Switch Rating: Not less than 800-VA fluorescent at 120 V, 1200-VA fluorescent at 277 V, and 800-W incandescent, and 1200-VA LED.

  - WALL-SWITCH SENSOR:

    - Range: 180-degree field of view, coverage shall be adequate for application.

    - Sensing Technology: Dual technology.

    - Switch Type: Field selectable for automatic on or manual on, with automatic off.

    - Voltage: Match the circuit voltage.

    - Concealed, field-adjustable, "off" time-delay selector at up to 30 minutes.

    - Field adjustable sensitivity adjustment.

  - LIGHTING CONTACTORS

    - Description: Electrically operated and mechanically held combination-type lighting contactors with nonfused disconnect, complying with NEMA ICS 2 and UL 508.

      - Current Rating for Switching: Listing or rating consistent with type of load served, including tungsten filament, inductive, and high-inrush ballast (ballast with 15 percent or less total harmonic distortion of normal load current).

      - Fault Current Withstand Rating: Equal to or exceeding the available fault current at the point of installation.

Specify coil operating voltage below.

      - Coil operating voltage: [120][277][480]V 60Hz.

      - Auxiliary Contacts: Field convertible contacts with normally open contacts and normally closed indicators.

      - Poles: As required to match circuit configuration. 12-pole maximum.

      - Enclosure: NEMA ICS 6 and NEMA 250, as required to match conditions. Fabricate enclosure from steel finished with gray. Interior NEMA Type 1, Exterior NEMA Type [3R][4X].

      - Provide field convertible contacts with N.O. and N.C. indicators.

      - Provide contactors in enclosure with mounting brackets.

  - EMERGENCY SHUNT RELAY

    - Description: Normally closed, electrically held relay, arranged for wiring in parallel with manual or automatic switching contacts; complying with UL 924.

      - Coil Rating: Voltage to match lighting circuit.

  - LOW-VOLTAGE WIRING

    - Comply with requirements in Section 26 05 23 - Control/Signal Transmission Media, and with device manufacturers requirements and recommendations.

- EXECUTION

  - SENSOR INSTALLATION

    - Coordinate layout and installation of ceiling-mounted devices with other construction that penetrates ceilings or is supported by them, including light fixtures, HVAC equipment, smoke detectors, fire-suppression systems, and partition assemblies. Comply with device manufacturer’s recommendations for distance from HVAC equipment.

    - Install and aim sensors in locations to achieve not less than 90 percent coverage of areas indicated. Do not exceed coverage limits specified in manufacturer's written instructions.

    - Outdoor Photoelectric Cells shall be oriented north and shall be directed to avoid detection of artificial light source.

    - Installation shall comply with sensor manufacturer’s recommendations.

  - CONTACTOR INSTALLATION

Coordinate this Article with Drawings.

    - Mount electrically held lighting contactors with elastomeric isolator pads to eliminate structure-borne vibration, unless contactors are installed in an enclosure with factory-installed vibration isolators.

    - Install lighting contactors in NEMA enclosure appropriate for location. Provide disconnecting means and overcurrent protection at contactor enclosures.

    - Mount control equipment according to manufacturer’s written instructions and requirements in Section 26 05 48 - Seismic Controls for Electrical and Communication Work.

  - WIRING INSTALLATION

    - Install wiring as specified in Section 26 05 19 - 600 Volt or Less Wire and Cable for low-voltage connections and Section 26 05 23 - Control/Signal Transmission Media for digital circuits.

    - Wiring within Enclosures: Comply with NECA 1. Separate power-limited and non-power-limited conductors according to conductor manufacturer's written instructions. Wires in enclosures shall be neatly arranged and protected from damage.

    - Size conductors according to lighting control device manufacturer's written instructions unless otherwise indicated.

    - Splices, Taps, and Terminations: Make connections only on numbered terminal strips in junction, pull, and outlet boxes; terminal cabinets; and equipment enclosures.

    - Connections: Tighten electrical connectors and terminals according to manufacturer’s published torque-tightening values. If manufacturer’s torque values are not indicated, use those specified in UL 486A.

  - IDENTIFICATION

    - Identify components and power and control wiring according to Section 26 05 53 - Electrical Identification.

    - Identify controlled circuits in lighting contactors.

    - Identify circuits or luminaires controlled by photoelectric and occupancy sensors at each sensor.

  - FIELD QUALITY CONTROL

    - Testing Agency: Engage a qualified testing agency to evaluate lighting control devices and perform tests and inspections.

    - Manufacturer’s Field Services: Engage a factory-authorized service representative to test and inspect components, assemblies, and equipment installations, including connections if required based on project scope.

    - Schedule visual and mechanical inspections and electrical tests with at least seven days’ advance notice.

Delete non-applicable items below.

    - Inspect control components for defects and physical damage, testing laboratory labeling, and nameplate compliance with the Contract Documents.

    - Check tightness of electrical connections with torque wrench calibrated within previous six months. Use manufacturer’s recommended torque values.

    - Verify settings of photoelectric devices with photometer calibrated within previous six months.

    - Perform the following calibration, tests and inspections:

      - Occupancy Sensors:

        - Visually check placement and aiming of sensors and LED activity.

        - Verify that wiring type, technique, connections, and polarity are correct.

        - Test sensor function:

          - Motion

            - Set sensitivity to Minimum. Set time delay to Minimum. Verify OFF.

            - Adjust sensitivity to desired setting. Verify ON with motion.

            - Adjust time delay to desired setting. Walk-test room for sensitivity.

      - Daylight Sensors

        - Visually check placement and aiming of sensors and LED display.

        - Verify that wiring type, technique, connections and polarity are correct.

        - All room finishes and furniture must be installed prior to start-up, calibration and testing. If a desk or table is within the area viewed by the photocell, then the desk should be unpacked, and the surface cleaned prior to final calibration.

        - Any window treatment must be installed and operable prior to start-up. Blinds must be positioned as they would be under normal conditions.

        - Do not calibrate dimming controls under overcast skies. Controls adjusted under these conditions are likely to over-dim the lights under sunny conditions.

        - Calibrate and test sensor function:

          - Adjust deadband and cutoff levels based on project requirements.

          - Set light level to Minimum. Set sensitivity level to Minimum. Set time delay to Minimum. Verify OFF.

          - Adjust sensitivity to desired setting. Cover sensor lens. Verify ON.

          - Adjust Light Level to desired setting.

          - Adjust time delay to desired setting.

    - Adjust sensors to meet project requirements. Replace damaged and malfunctioning controls and equipment.

    - Lighting control devices will be considered defective if they do not pass tests and inspections.

    - Prepare test and inspection reports. Include list of devices tested and indication of correct function. Note device settings for each device.

  - ADJUSTING

    - Occupancy Adjustments: When requested within 12 months from date of Substantial Completion, provide on-site assistance in adjusting sensors to suit actual occupied conditions. Provide up to two visits to Project during other-than-normal occupancy hours for this purpose.

      - For occupancy and motion sensors, verify operation at outer limits of detector range. Set time delay to suit Owner's operations.

      - For daylighting controls, adjust set points and deadband controls to suit Owner's operations.

  - CLEANING

    - Cleaning: Clean equipment and devices internally and externally using methods and materials recommended by manufacturers, and repair damaged finishes.

  - DEMONSTRATION

    - Coordinate demonstration of products specified in this Section with demonstration requirements for low-voltage, programmable lighting control systems specified in Section 260943.13 "Addressable-Fixture Lighting Controls" and Section 260943.23 "Relay-Based Lighting Controls."

    - Engage a factory-authorized service representative to train Port maintenance personnel to adjust, operate, and maintain lighting control devices.

  - COMMISIONING

    - Provide controls commissioning according to Washington State Energy Code requirements.

- MEASUREMENT AND PAYMENT

  - GENERAL

    - No separate measurement or payment will be made for the Work required by this section. The cost for this portion of the Work will be considered incidental to, and included in the payments made for the applicable bid items in the [Schedule of Unit Prices] [Lump Sum price bid for the Project].

End of Section

Revision History:

05/01/2014 Conversion to 2004 CSI Numbering System

10/15/2014 Added Sole Source and Salient Characteristics Note to Part 2 and revisions

09/20/2021 Revised per F&I Standard